## 6.4.36
Table 6.4.36
EFFLUENT STANDARDS(g)
Parameter | Unit | Water Body Classification
|  | AA | A | B | C | D | SA | SB | SC | SD
*Ammonia as NH3-N | mg/L | NDA | 2 | 3 | 4 | 9 | NDA | 3 | 4 | 9
BOD | mg/L | NDA | 20 | 30 | 50 | 120 | NDA | 30 | 100 | 150
*Boron | mg/L | NDA | 4 | 4 | 4 | 12 | NDA | 4 | 25 | 100
Chloride | mg/L | NDA | 350 | 350 | 450 | 500 | NDA | n/a | n/a | n/a
COD | mg/L | NDA | 60 | 60 | 100 | 200 | NDA | 60 | 200 | 300
Color | TCU | NDA | 100 | 100 | 150 | 300 | NDA | 100 | 150 | 300
Cyanide as Free Cyanide | mg/L | NDA | 0.14 | 0.14 | 0.2 | 0.4 | NDA | 0.04 | 0.2 | 0.4
Fluoride | mg/L | NDA | 2 | 2 | 2 | 4 | NDA | 3 | 3 | 6
Nitrate as NO3-N | mg/L | NDA | 14 | 14 | 14 | 30 | NDA | 20 | 20 | 30
pH (Range) |  | NDA | 6.0-9.0 | 6.0-9.0 | 6.0-9.5 | 5.5-9.5 | NDA | 6.5-9.0 | 6.0-9.0 | 5.5-9.5
*Phosphate | mg/L | NDA | 1 | 1.5 | 4 | 10 | NDA | 2 | 4 | 10
Selenium | mg/L | NDA | 0.02 | 0.02 | 0.04 | 0.08 | NDA | 0.02 | 0.2 | 0.4
*Sulfate | mg/L | NDA | 500 | 500 | 550 | 1000 | - | - | - | -
Surfactants (MBAS) | mg/L | NDA | 2 | 3 | 15 | 30 | NDA | 3 | 15 | 30
Temperature(h) | °C change | NDA | 3 | 3 | 3 | 3 | NDA | 3 | 3 | 3
Total Suspended Solids | mg/L | NDA | 70 | 85 | 100 | 150 | NDA | 70 | 100 | 150
Arsenic | mg/L | NDA | 0.02 | 0.02 | 0.04 | 0.08 | NDA | 0.02 | 0.04 | 0.08
Barium | mg/L | NDA | 1.5 | 1.5 | 6 | 8 | NDA | 1.5 | 2 | 8
Cadmium | mg/L | NDA | 0.006 | 0.006 | 0.01 | 0.02 | NDA | 0.006 | 0.01 | 0.02
Chromium as Hexavalent Chromium (Cr6+) | mg/L | NDA | 0.02 | 0.02 | 0.02 | 0.04 | NDA | 0.1 | 0.1 | 0.2
*Total Copper | mg/L | NDA | 1 | 1 | 1 | 2 | NDA | 1 | 1 | 2
Iron | mg/L | NDA | 5 | 5 | 7.5 | 35 | NDA | 7.5 | 7.5 | 35
Lead | mg/L | NDA | 0.02 | 0.02 | 0.1 | 0.2 | NDA | 0.02 | 0.1 | 0.2
Manganese | mg/L | NDA | 2 | 2 | 2 | 20 | NDA | 4 | 4 | 40
Mercury | mg/L | NDA | 0.002 | 0.002 | 0.004 | 0.008 | NDA | 0.002 | 0.004 | 0.008
Nickel | mg/L | NDA | 0.1 | 0.2 | 1 | 5 | NDA | 0.2 | 0.3 | 1.5
Zinc | mg/L | NDA | 4 | 4 | 4 | 8 | NDA | 0.1 | 1.5 | 3
Benzo(a)pyrene | µg/L | NDA | 1.5 | 1.5 | 3 | 6 | NDA | 1.5 | 3 | 6
BTEX
Benzene | mg/L | NDA | 0.1 | 0.1 | 0.5 | 5 | NDA | 0.1 | 0.5 | 5
Toluene | mg/L | NDA | 3.5 | 5 | 20 | 25 | NDA | 5 | 20 | 25
Ethylbenzene | mg/L | NDA | 1.5 | 1.5 | 7.5 | 10 | NDA | 1 | 7.5 | 10
Xylenes | mg/L | NDA | 5 | 5 | 15 | 18 | NDA | 5 | 15 | 18
Malathion (Organophosphate) | µg/L | NDA | 1 | 1 | 3 | 6 | NDA | 1 | 3 | 6
Oil and Grease | mg/L | NDA | 5 | 5 | 5 | 15 | NDA | 5 | 10 | 15
Polychlorinated Biphenyls(i) | µg/L | NDA | <0.1 | <0.1 | <0.1 | <0.1 | NDA | <0.1 | <0.1 | <0.1
Phenol & Phenolic Substances(j) | mg/L | NDA | 0.01 | 0.01 | 0.5 | 5 | NDA | 0.01 | 0.5 | 5
Trichloroethylene | mg/L | NDA | 0.7 | 0.7 | 9 | 20 | NDA | 0.7 | 9 | 20
Total Organochlorine Pesticides(k) | µg/L | NDA | <0.419 | 50 | 50 | 50 | NDA | 50 | 50 | 50
Aldrin | µg/L | NDA | <0.02 | <0.02 | <0.02 | <0.02 | NDA | <0.02 | <0.02 | <0.02
Chlordane | µg/L | NDA | <0.02 | <0.02 | <0.02 | <0.02 | NDA | <0.02 | <0.02 | <0.02
DDT | µg/L | NDA | <0.04 | <0.04 | <0.04 | <0.04 | NDA | <0.04 | <0.04 | <0.04
Dieldrin | µg/L | NDA | <0.02 | <0.02 | <0.02 | <0.02 | NDA | <0.02 | <0.02 | <0.02
Endrin | µg/L | NDA | <0.02 | <0.02 | <0.02 | <0.02 | NDA | <0.02 | <0.02 | <0.02
Heptachlor | µg/L | NDA | <0.02 | <0.02 | <0.02 | <0.02 | NDA | <0.02 | <0.02 | <0.02
Total Organochlorine Pesticides (continued)
Lindane | µg/L | NDA | <0.02 | <0.02 | <0.02 | <0.02 | NDA | <0.02 | <0.02 | <0.02
Metoxychlor | µg/L | NDA | <0.03 | <0.03 | <0.03 | <0.03 | NDA | <0.03 | <0.03 | <0.03
Toxaphene | µg/L | NDA | <0.03 | <0.03 | <0.03 | <0.03 | NDA | <0.03 | <0.03 | <0.03
Notes:
NDA - No Discharge Allowed
(-) - means no recommended values due to the natural occurrence in marine/brackish waters
* - updated as per Department of Environment and Natural Resources Administrative Order No. 2021-19
(g) GES values are maximum allowable limit.
(h) GES values for temperature refer to the temperature difference of the background value and discharge point. Specific sampling locations shall be established based on the EMB Ambient Water and Effluent Quality Monitoring Manual. Sampling locations for temperature monitoring, established and approved by EMB, prior to this order shall remain valid.
(i) PCBs include the nine Aroclors and 19 individual PCB congeners described in Section 6.1 of DAO 2016-08.
(j) Phenols include 2-chlorophenol, 2, 4-dichlorophenol, and 2,4,6-trichlorophenol
(k) When monitoring for Class A waters, the individual organochlorine pesticides shall be monitored. For Class B, C, D, SB, SC, SD, Total Organochlorine Pesticides shall be monitored, which refers to the organochlorine pesticies listed in Table 0-2 plus BHC (α,β,δ,γ), 4,4'DDD, 4,4'DDE, Endosulfan (I, II, and sulfate).
Source: Department of Environment and Natural Resources Administrative Order No. 2016-08
Department of Environment and Natural Resources Administrative Order No. 2021-19